## Index
Work Sheet | INDEX: TIME SERIES DATA - SA Power Networks - PERFORMANCE
TSD_001 | OP 1.1 - SA Power Networks’ performance against time to respond to telephone calls
TSD_002 | OP 1.2 - SA Power Networks’ performance against time to respond to written enquiries
TSD_003 | OP 1.3 - SA Power Networks’ performance against time to respond to enquiries requesting a written response ** NOT CURRENT
TSD_004 | OP 1.4 - SA Power Networks’ planned interruption notification performance ** NOT CURRENT
TSD_005 | OP 2.1 - Distribution Code Reliability Performance Targets, Measured Overall Performance of SA Power Networks (SAIDI)
TSD_006 | OP 2.2 - Statewide SAIDI attributable to transmission and Generation outages
TSD_007 | OP 2.3 - Distribution Code Reliability Performance Targets, Measured Overall Performance of SA Power Networks (SAIFI)
TSD_008 | OP 2.4 - Severe Weather Events - Total Overall and Normalised State-wide HV SAIDI
TSD_009 | OP 2.6 - Interruption Cause Analysis for SA Power Networks, Distribution Network (based on contribution to state-wide SAIDI)
TSD_010 | Adelaide Business Area Reliability Performance
TSD_011 | Major Metropolitan Areas Reliability Performance
TSD_012 | Central Region Reliability Performance
TSD_013 | Eastern Hills/Fleurieu Peninsula Region Reliability Performance
TSD_014 | Upper North/Eyre Peninsula Region Reliability Performance
TSD_015 | South East Region Reliability Performance
TSD_016 | Kangaroo Island Region Reliability Performance
TSD_017 | OP 3.1 - Quality of Supply
TSD_018 | OP 3.2 - SA Power Networks’ Customer Compensation payments for Quality of Service (voltage variation)
TSD_019 | OP 4.1 - SA Power Networks’ Performance Against Timeliness of Appointments
TSD_020 | OP 4.2 - SA Power Networks’ Performance Against Promptness of Connection
TSD_021 | OP 4.3 - SA Power Networks’ Performance Against Timeliness of Street Light Repairs – Adelaide Business Area and Major Metropolitan Areas
TSD_022 | OP 4.4 - SA Power Networks’ Performance Against Timeliness of Street Light Repairs – Country Areas
TSD_023 | OP 4.5 - GSL: Frequency of Supply Interruptions
TSD_024 | OP 4.6 - GSL: Duration of Supply Interruptions
TSD_025 | OP 6.1 - SA Power Networks’ Network Energy Losses
TSD_026 | Distribution Code Reliability Performance Targets, Measured Overall Performance of SA Power Networks (CAIDI) ** NOT CURRENT
TSD_027 | SA Power Networks’ performance against Time to Restore Supply service standards, Distribution Code ** NOT CURRENT
TSD_028 | Summary - Performance against Guaranteed Service Levels (Customer Payments)
Work Sheet | INDEX: TIME SERIES DATA - ELECTRANET - PERFORMANCE
TSD_030 | OP1 – Connection point restoration Standards
TSD_031 | OP2 – Power System Incidents
TSD_032 | OP3 – Operational Statistics – RELIABILITY (incorporating the information requirements of the Technical Regulator)
TSD_033 | OP3 – Operational Statistics – STATISTICAL (incorporating the information requirements of the Technical Regulator)
TSD_034 | OP3 – Operational Statistics - TECHNICAL - (incorporating the information requirements of the Technical Regulator)
TSD_035 | Interconnector Import/Export details - Heywood and Murraylink Interconnectors ** NOT CURRENT
TSD_036 | OP4 - Exit Point Demand Forecast (3-year forward forecast) ** NOT CURRENT
Work Sheet | INDEX: TIME SERIES DATA - ENVESTRA - PERFORMANCE (Australian Gas Networks data provided separately)
TSD_040 | OP – Promptness of connection - **NOT CURRENT
TSD_041 | OP – Network Extension and Expansion Charges - **NOT CURRENT
TSD_042 | OP – Interruptions - **NOT CURRENT
TSD_043 | OP 1 – Major Interruptions**NOT CURRENT
TSD_044 | OP 2 – Statistical Information - Gas quantities Table (a) and Table (g)**NOT CURRENT
TSD_045 | OP 3 – Technical Information - Table (f) Other Technical Information **NOT CURRENT
TSD_046 | OP 4 – Unaccounted for Gas and Mains Replacement Program**NOT CURRENT
TSD_047 | OP 5 – Complaints**NOT CURRENT
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO
GOTO

## TSD_001
OP 1.1 - SA Power Networks’ performance against time to respond to telephone calls
Measure | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Number of calls | 562608 | 440913 | 463199 | 446008 | 427608 | 560374 | 432871 | 462867 | 599389 | 643570 | 845689 | 671066 | 618410 | 656524 | 475052 | 432151 | 606753 | 393806 | 394810 | 352430
Percentage of calls answered within 30 seconds | 86% | 87.1% | 85% | 88%(1) | 89% | 85% | 89.3% | 88.7% | 89% | 91% | 86% | 89% | 89% | 88% | 91% | 87% | 86.6% | 89.8% | 90% | 90%
(1) In 2003/04, the Commission reviewed the method of compiling telephone response data, and in particular the treatment of the integrated voice response (IVR) service offered by SA Power Networks. The data for 2000/01, 2001/02 and 2002/03 has been recalculated on the basis of the new method.
Back to Index

## TSD_002
OP 1.2 - SA Power Networks’ performance against time to respond to written enquiries
Measure | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Number of written enquiries | 846 | 1424 | 1481 | 1713 | 2013 | 5122 | 3543 | 3865 | 3479 | 3049 | 4107 | 4002 | 3783 | 5000 | 2709 | 723 | 1331 | 2237 | 3881 | 2269
% written enquiries responded to within 5 business days | 96.1% | 98.4% | 99.1% | 96.8% | 99.2% | 95.2% | 98.1% | 97.2% | 95.8% | 99.1% | 98% | 98% | 98% | 99% | 98.4% | 99% | 99% | 98% | 99% | 96%
Back to Index

## TSD_003
OP 1.3 - SA Power Networks’ performance against time to respond to enquiries requesting a written response
Measure | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17
Number of enquiries seeking a written explanation for interruptions to supply | 409 | 219 | 192 | 349 | 146 | 244 | 143 | 139 | 94 | 122 | 320 | 63 | 29 | N/A | N/A | N/A | N/A
Percentage of enquiries responded to in writing within 20 business days | 70.4% | 94.1% | 94.8% | 92.6% | 93.8% | 88.9% | 95.1% | 94.2% | 96.8% | 99% | 97% | 100% | 93% | N/A | N/A | N/A | N/A
Note: From 2013, network performance in regard to written explanations to interruptions to supply is now reported under the national framework (NECF)
Back to Index

## TSD_004
OP 1.4 - SA Power Networks’ planned interruption notification performance
Measure | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17
Number of planned interruptions | 2338 | 2212 | 1301 | 1390 | 1443 | 1791 | 1487 | 1377 | 1212 | 1327 | 1789 | 3737 | 4309 | N/A | N/A | N/A | N/A
% planned interruptions where written notification to affected customers is more than 4 business days | 98.7% | 97.9% | 97.8% | 97.8% | 98.1% | 98.2% | 98.9% | 98.8% | 97.4% | 94.8% | 97.4% | 97% | 96% | N/A | N/A | N/A | N/A
Note: From 2013, network performance in regard to planned interruptions is now reported under the national framework (NECF)
Back to Index

## TSD_005
OP 2.1 - Distribution Code Reliability Performance Targets, Measured Overall Performance of SA Power Networks (SAIDI - Minutes)
Each of the targets specified in the table is a baseline target in the PI Scheme for SA Power Networks as defined in the Electricity Distribution Code. The SAIFI and SAIDI targets for the Urban, Rural and Remote regions are also specified as “best endeavours” standards in the Distribution Code. Figures reported are normalised.
2016-20 TARGETS
Region |  | 2015/2016 | 2016/2017 | 2017/2018 | 2018/2019 | 2019/2020
CBD Feeder | 15 | 2.3 | 16 | 43 | 13 | 33.3
Urban Feeder | 120 | 97.9 | 111 | 96 | 99 | 84.7
Long Rural Feeder | 220 | 174.8 | 230 | 155 | 181 | 144.7
Short Rural Feeder | 300 | 289.4 | 264 | 269 | 333 | 260.4
Total (State-wide) |  | 139 | 151.4 | 132 | 146 | 119.9
2015-20 MONITORING PURPOSES ONLY
Region |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Adelaide Business Area | - | 2.3 | 16.2 | 42.6 | 13 | 33
Major Metropolitan Areas | - | 98.2 | 112 | 96.1 | 101 | 86
Central | - | 193.2 | 194 | 148.6 | 211 | 151
Eastern Hills & Fleurieu Peninsula | - | 205.1 | 323.7 | 205.3 | 212.1 | 182
Upper North & Eyre Peninsula | - | 426.9 | 309.6 | 357.6 | 414.8 | 197
South East | - | 201.2 | 157.5 | 304.3 | 285 | 301
Kangaroo Island | - | 385.8 | 273.3 | 205.9 | 590.4 | 1299
Total (State-wide) | - | - | - | - | - | -
2010-15 TARGETS
Region |  | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
Adelaide Business Area | 25 | 19 | 11.7 | 12.6 | 9 | 10.9
Major Metropolitan Areas | 130 | 218 | 103.5 | 143.4 | 265 | 104.5
Central | 260 | 582 | 278.8 | 299.3 | 542 | 279.7
Eastern Hills & Fleurieu Peninsula | 295 | 465 | 320.2 | 316.6 | 425 | 229
Upper North & Eyre Peninsula | 425 | 841 | 381.8 | 474.4 | 390 | 353.8
South East | 295 | 277 | 243.8 | 411.4 | 428 | 198.9
Kangaroo Island | 450 | 198 | 336.7 | 686.6 | 385 | 266.4
Total (State-wide) | 179 | 311 | 158.9 | 201.3 | 287 | 151.9
2000-10 TARGET
Region |  | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
Adelaide Business Area | 25 | 45 | 11 | 15 | 29 | 19 | 10 | 7 | 16 | 23 | 1
Major Metropolitan Areas | 115 | 110 | 109 | 122 | 118 | 108 | 143 | 118 | 109 | 118 | 147
Central | 240 | 234 | 208 | 348 | 186 | 355 | 239 | 267 | 202 | 225 | 337
Eastern Hills & Fleurieu Peninsula | 350 | 333 | 296 | 382 | 389 | 379 | 414 | 381 | 252 | 326 | 438
Upper North & Eyre Peninsula | 370 | 399 | 293 | 341 | 303 | 399 | 610 | 481 | 361 | 375 | 632
South East | 330 | 524 | 277 | 347 | 345 | 230 | 256 | 489 | 328 | 226 | 278
Kangaroo Island | 450 | 932 | 1084 | 905 | 1960 | 290 | 1354 | 510 | 565 | 232 | 371
Total (State-wide) | 165 | 164 | 147 | 184 | 164 | 169 | 199 | 184 | 150 | 161 | 217
Back to Index

## TSD_006
OP 2.2 - State-wide SAIDI (normalised) attributable to generation and transmission outages
| 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
SAIDI (as reported in OP 2.1) | 159.66 | 143.32 | 178 | 159 | 164.11 | 193.3 | 177.6 | 144.5 | 155.1 | 208.6 | 310.8 | 158.9 | 201.4 | 287 | 151.9 | 139 | 151.4 | 131.7 | 146.4 | 119.9
SAIDI attributed to transmission outages | 6.22 | 5.23 | 15 | 51.3 | 42.2 | 7.52 | 7.83 | 2.43 | 11.1 | 8.9 | 6.6 | 10.7 | 31.1 | 2.7 | 1.6 | 11.8 | 21.4 | 5.6 | 3.3 | 6.2
SAIDI attributed to generation outages | 1.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5 | 15.8 | 0 | 0 | 0
TOTAL | 167.8 | 148.55 | 193 | 210.2 | 206.31 | 200.8 | 185.54 | 147.85 | 174.6 | 217.5 | 317.4 | 169.6 | 232.5 | 289.7 | 153.5 | 160.3 | 188.6 | 137.3 | 149.7 | 126.1
Back to Index

## TSD_007
OP 2.3 - Distribution Code Reliability Performance Targets, Measured Overall Performance of SA Power Networks (SAIFI - Frequency p.a.)
Each of the targets specified in the table is a baseline target in the PI Scheme for SA Power Networks as defined in the Electricity Distribution Code. The SAIFI and SAIDI targets for the Urban, Rural and Remote regions are also specified as “best endeavours” standards in the Distribution Code. Figures reported are normalised.
2015-20 TARGETS
Region |  | 2015/2016 | 2016/2017 | 2017/2018 | 2018/2019 | 2019/2020
CBD Feeder | 0.15 | 0.024 | 0.114 | 0.41 | 0.103 | 0.19
Urban Feeder | 1.3 | 1.038 | 1.115 | 1.06 | 0.949 | 0.78
Long Rural Feeder | 1.85 | 1.482 | 1.712 | 1.48 | 1.46 | 1.17
Short Rural Feeder | 1.95 | 1.7 | 1.428 | 1.2 | 1.682 | 1.32
Total (State-wide) |  | 1.201 | 1.244 | 1.14 | 1.131 | 0.91
2015-20 MONITORING PURPOSES ONLY
Region |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Adelaide Business Area | - | 0.024 | 0.114 | 0.407 | 0.1 | 0.19
Major Metropolitan Areas | - | 1.106 | 1.145 | 1.07 | 0.97 | 0.8
Central | - | 1.503 | 1.404 | 0.986 | 1.27 | 0.98
Eastern Hills & Fleurieu Peninsula | - | 1.725 | 1.919 | 1.363 | 1.72 | 1.16
Upper North & Eyre Peninsula | - | 1.629 | 1.074 | 1.618 | 1.26 | 1.03
South East | - | 1.43 | 1.175 | 2.057 | 1.86 | 2.03
Kangaroo Island | - | 4.297 | 2.918 | 0.912 | 4.73 | 3.28
Total (State-wide) | - | - | - | - | - | -
2010-15 TARGETS
Region |  | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
Adelaide Business Area | 0.25 | 0.14 | 0.141 | 0.16 | 0.115 | 0.151
Major Metropolitan Areas | 1.45 | 1.79 | 1.208 | 1.45 | 1.719 | 1.121
Central | 1.8 | 2.74 | 1.609 | 1.59 | 1.593 | 1.361
Eastern Hills & Fleurieu Peninsula | 2.8 | 3.29 | 2.525 | 2.27 | 2.901 | 1.575
Upper North & Eyre Peninsula | 2.3 | 2.72 | 1.711 | 1.61 | 1.691 | 1.432
South East | 2.5 | 1.67 | 2.012 | 2.56 | 2.445 | 1.667
Kangaroo Island | N/A | 2.45 | 2.346 | 3.97 | 2.851 | 3.177
Total (State-wide) | 1.68 | 2.05 | 1.404 | 1.57 | 1.828 | 1.228
Region | TARGET | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
Adelaide Business Area | 0.3 | 0.62 | 0.09 | 0.22 | 0.27 | 0.22 | 0.2 | 0.08 | 0.13 | 0.19 | 0.02
Major Metropolitan Areas | 1.4 | 1.32 | 1.38 | 1.56 | 1.46 | 1.32 | 1.61 | 1.47 | 1.23 | 1.26 | 1.56
Central | 2.1 | 2.25 | 1.84 | 2.42 | 1.72 | 2.9 | 1.64 | 2.02 | 1.49 | 1.84 | 2.28
Eastern Hills & Fleurieu Peninsula | 3.3 | 2.81 | 3.04 | 3.43 | 3.73 | 3.4 | 3.72 | 2.59 | 2.39 | 3.11 | 3.49
Upper North & Eyre Peninsula | 2.5 | 3.37 | 2.9 | 2.24 | 2.1 | 2.71 | 3.31 | 2.3 | 1.99 | 2.49 | 2.52
South East | 2.7 | 3.61 | 2.06 | 2.07 | 2.08 | 2.35 | 2.36 | 3.78 | 2.65 | 1.86 | 2.54
Kangaroo Island | N/A | 3.83 | 9.83 | 8.93 | 13.74 | 3.04 | 9.34 | 7.33 | 7.85 | 2.95 | 4.89
Total (State-wide) |  | 1.69 | 1.64 | 1.84 | 1.69 | 1.71 | 1.85 | 1.75 | 1.45 | 1.53 | 1.85
Back to Index

## TSD_008
OP 2.4 - Severe Weather Events - Total Overall and Normalised Statewide unplanned SAIDI
DETAIL | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Normalised SAIDI (Annual Performance report) | 139 | 151.4 | 131.7 | 146.4 | 119.9
No. of Major Event Days (MED's) | 1 | 9 | 0 | 4 | 3
Total SAIDI for Major Event Days | 8.7 | 329.5 | 0 | 49.4 | 29.9
Overall SAIDI | 147.7 | 480.9 | 131.7 | 195.8 | 149.8
From 2015-16 Major Event Days (MED) are reported rather than the number of Severe Weather Events
DETAIL | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16
Overall SAIDI (Annual Performance report) | 158.9 | 142.9 | 179 | 158.8 | 164.2 | 193.3 | 177.6 | 144.5 | 155.1 | 208.6 | 310.8 | 158.9 | 201.3 | 287 | 151.9
No. of Severe Weather Events | 2 | 2 | 6 | 3 | 3 | 7 | 7 | 2 | 4 | 10 | 7 | 3 | 5 | 7 | 3
Total SAIDI for Severe Weather events | 12.4 | 16.6 | 50.9 | 15.1 | 26.8 | 57.7 | 37.7 | 13 | 31.9 | 58.2 | 173 | 31.1 | 64 | 132.1 | 33.4
Normalised SAIDI | 146.5 | 126.3 | 128.1 | 143.7 | 137.4 | 135.6 | 139.9 | 131.5 | 123.2 | 150.4 | 137.8 | 127.8 | 137.3 | 154.9 | 118.5
Note: For 2005/06 to 2009/10, SAIDI is for High Voltage network only. For 2010/11 onwards, includes Low Voltage SAIDI
Back to Index

## TSD_009
OP 2.6 - Interruption cause analysis for SA Power Networks' distribution network (based on contribution to state-wide SAIDI)
| Cause (excl MEDs*) | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | Ave
| Weather | 32% | 37% | 45% | 35% | 35% | 41% | 28% | 34% | 26% | 32% | 24% | 23% | 21% | 22% | 18% | 20% | 23% | 19% | 22% | 14% | 20.6%
| Equipment Failure | 29% | 30% | 23% | 32% | 26% | 21% | 25% | 26% | 24% | 30% | 26% | 21% | 23% | 24% | 19% | 22% | 23% | 23% | 19% | 28% | 22.8%
| Planned Interruption | 6% | 9% | 7% | 8% | 10% | 6% | 9% | 10% | 10% | 7% | 24% | 32% | 34% | 30% | 41% | 36% | 30% | 33% | 38% | 37% | 33.5%
| Operational Factors | 6% | 2% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 0.5% | 1% | 0.6% | 0.5% | 0.8% | 0.6% | 0.6% | 0.5% | 0.5% | 2% | 1% | 0.81%
| Third Party | 12% | 13% | 12% | 10% | 13% | 9% | 11% | 9% | 14% | 8% | 8% | 9% | 8% | 9% | 8% | 8% | 8% | 11% | 8% | 7% | 8.4%
| Unknown | 12% | 8% | 11% | 11% | 14% | 21% | 24% | 17% | 24% | 22% | 17% | 14% | 13% | 14% | 13% | 14% | 15% | 13% | 11% | 13% | 13.7%
| Other | 3% | 1% | 1% | 2% | 1% | 1% | 2% | 3% | 1% | 0.4% | 0.1% | 0.5% | 0.7% | 0.1% | 0.3% | 0.2% | 0.3% | 0.4% | 0.3% | 0.4% | 0.33%
*MEDs - major event days
Back to Index

## TSD_010
Adelaide Business Area Reliability Performance
From 2015-16, SA Power Networks is not measured on performance in individual regions. Referto OP 2.1 and OP 2.3 for overall regional monitoring.
Performance Measure | TARGET | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
SAIDI | 25 | 45 | 11 | 15 | 29 | 19 | 10 | 7 | 16 | 23 | 1
SAIFI | 0.3 | 0.62 | 0.09 | 0.22 | 0.27 | 0.22 | 0.2 | 0.08 | 0.13 | 0.19 | 0.02
CAIDI (Implied target) | 80 | 73 | 122 | 71 | 108 | 86 | 53 | 88 | 125 | 123 | 52
MAIFI (frequency)(1) | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0
Restoration of Supply | 90% within 2h | 94% | 59% | 95% | 93% | 71% | 92% | 89% | 37% | 65% | 99%
Restoration of Supply | 95% within 3h | 96% | 93% | 97% | 100% | 95% | 100% | 99% | 100% | 69% | 99%
Annual SAIDI Severe Weather Events (min)(2) | - | - | - | - | - | - | - | 0 | 0 | 2.1 | 0
(1) Momentary Interruptions per Customer (MAIFI) means the total number of momentary interruptions (of less than 60 seconds duration) divided by the number of customers.
(2) A Severe Weather Event is defined as a weather related event where the contribution to regional SAIDI was the greater of three (3) minutes, or three (3) per cent of the Regional SAIDI standard in clause 1.1.3.1 of the Electricity Distribution Code.
2010-15 TARGETS
Performance Measure |  | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
SAIDI | 25 | 18.8 | 11.7 | 12.6 | 9 | 10.9
SAIFI | 0.25 | 0.136 | 0.141 | 0.16 | 0.115 | 0.151
CAIDI (Implied target) | N/A | 138.2353 | 82.9787 | 78.75 | 78.2609 | 72.1854
Annual SAIDI Severe Weather Events (min) | - | 0 | 0 | 0 | 0 | 0
The Commission is not collecting MAIFI nor Restoration of Supply data during the current regulatory period 2010-2015. Subject to further monitoring and future AER reporting requirements.
Back to Index

## TSD_011
Major Metropolitan Areas Reliability Performance
From 2015-16, SA Power Networks is not measured on performance in individual regions. Referto OP 2.1 and OP 2.3 for overall regional monitoring.
Performance Measure | TARGET | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
SAIDI | 115 | 110 | 109 | 122 | 118 | 108 | 143 | 118 | 109 | 118 | 147
SAIFI | 1.4 | 1.32 | 1.38 | 1.56 | 1.46 | 1.32 | 1.61 | 1.47 | 1.23 | 1.26 | 1.56
CAIDI (Implied target) | 82 | 83 | 79 | 78 | 81 | 82 | 89 | 80 | 89 | 94 | 94
MAIFI (frequency)(1) | N/A | N/A | N/A | N/A | N/A | N/A | 1.47 | 1.04 | 1.4 | 1.2 | 2.28
Restoration of Supply | 80% within 2h | 78% | 83% | 84% | 83% | 81% | 78% | 83% | 81% | 73% | 76%
Restoration of Supply | 90% within 3h | 91% | 94% | 95% | 84% | 92% | 92% | 94% | 94% | 92% | 90%
Annual SAIDI Severe Weather Events (min)(2) | - | - | - | - | - | - | - | 10.3 | 8.8 | 18.8 | 16
(1) Momentary Interruptions per Customer (MAIFI) means the total number of momentary interruptions (of less than 60 seconds duration) divided by the number of customers.
(2) A Severe Weather Event is defined as a weather related event where the contribution to regional SAIDI was the greater of three (3) minutes, or three (3) per cent of the Regional SAIDI standard in clause 1.1.3.1 of the Electricity Distribution Code.
2010-15 TARGETS
Performance Measure |  | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
SAIDI | 130 | 218.2 | 103.5 | 143.4 | 265 | 104.5
SAIFI | 1.45 | 1.79 | 1.208 | 1.45 | 1.719 | 1.121
CAIDI (Implied target) | N/A | 121.8994 | 85.6788 | 98.8966 | 154.1594 | 93.2203
Annual SAIDI Severe Weather Events (min) | - | 90.9 | 4.2 | 26.2 | 134.6 | 11
The Commission is not collecting MAIFI nor Restoration of Supply data during the current regulatory period 2010-2015. Subject to further monitoring and future AER reporting requirements.
Back to Index

## TSD_012
Central Region Reliability Performance
From 2015-16, SA Power Networks is not measured on performance in individual regions. Referto OP 2.1 and OP 2.3 for overall regional monitoring.
Performance Measure | TARGET | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
SAIDI | 240 | 234 | 208 | 348 | 186 | 355 | 239 | 267 | 202 | 225 | 337
SAIFI | 2.1 | 2.25 | 1.84 | 2.42 | 1.72 | 2.9 | 1.64 | 2.02 | 1.49 | 1.84 | 2.28
CAIDI (Implied target) | 115 | 73 | 122 | 71 | 108 | 86 | 53 | 88 | 136 | 122 | 148
MAIFI (frequency)(1) | N/A | N/A | N/A | N/A | N/A | N/A | 3.94 | 0.96 | 3.3 | 3.2 | 3.34
Restoration of Supply | 80% within 3h | 87% | 83% | 73% | 86% | 79% | 77% | 77% | 75% | 82% | 75%
Restoration of Supply | 90% within 5h | 97% | 95% | 89% | 97% | 92% | 92% | 91% | 93% | 94% | 89%
Annual SAIDI Severe Weather Events (min)(2) | - | - | - | - | - | - | - | 104.6 | 8.8 | 45.7 | 80.1
(1) Momentary Interruptions per Customer (MAIFI) means the total number of momentary interruptions (of less than 60 seconds duration) divided by the number of customers.
(2) A Severe Weather Event is defined as a weather related event where the contribution to regional SAIDI was the greater of three (3) minutes, or three (3) per cent of the Regional SAIDI standard in clause 1.1.3.1 of the Electricity Distribution Code.
2010-15 TARGETS
Performance Measure |  | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
SAIDI | 260 | 581.7 | 278.8 | 299.3 | 242.2 | 279.7
SAIFI | 1.8 | 2.741 | 1.609 | 1.59 | 1.593 | 1.361
CAIDI (Implied target) | N/A | 212.2218 | 173.2753 | 188.239 | 152.0402 | 205.5107
Annual SAIDI Severe Weather Events (min) | - | 358.8 | 122.6 | 152.3 | 63.7 | 13
The Commission is not collecting MAIFI nor Restoration of Supply data during the current regulatory period 2010-2015. Subject to further monitoring and future AER reporting requirements.
Back to Index

## TSD_013
Eastern Hills & Fleurieu Peninsula Region Reliability Performance
From 2015-16, SA Power Networks is not measured on performance in individual regions. Referto OP 2.1 and OP 2.3 for overall regional monitoring.
Performance Measure | TARGET | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
SAIDI | 350 | 333 | 296 | 382 | 389 | 379 | 414 | 381 | 252 | 326 | 438
SAIFI | 3.3 | 2.81 | 3.04 | 3.43 | 3.73 | 3.4 | 3.72 | 2.59 | 2.39 | 3.11 | 3.49
CAIDI (Implied target) | 105 | 118 | 97 | 111 | 104 | 112 | 111 | 147 | 106 | 105 | 126
MAIFI (frequency)(1) | N/A | N/A | N/A | N/A | N/A | N/A | 1.8 | 4.45 | 2.1 | 3.1 | 3.74
Restoration of Supply | 80% within 3h | 79% | 91% | 82% | 88% | 87% | 90% | 75% | 83% | 87% | 79%
Restoration of Supply | 90% within 4h | 90% | 97% | 93% | 92% | 92% | 93% | 83% | 92% | 91% | 90%
Annual SAIDI Severe Weather Events (min)(2) | - | - | - | - | - | - | - | 94.4 | 57.2 | 60.5 | 116.9
(1) Momentary Interruptions per Customer (MAIFI) means the total number of momentary interruptions (of less than 60 seconds duration) divided by the number of customers.
(2) A Severe Weather Event is defined as a weather related event where the contribution to regional SAIDI was the greater of three (3) minutes, or three (3) per cent of the Regional SAIDI standard in clause 1.1.3.1 of the Electricity Distribution Code.
2010-15 TARGETS
Performance Measure |  | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
SAIDI | 295 | 465.1 | 320.2 | 316.6 | 425.1 | 229
SAIFI | 2.8 | 3.285 | 2.525 | 2.27 | 2.901 | 1.575
CAIDI (Implied target) | N/A | 141.583 | 126.8119 | 139.4714 | 146.5357 | 145.3968
Annual SAIDI Severe Weather Events (min) | - | 204.2 | 90.9 | 143.3 | 107.8 | 19.9
The Commission is not collecting MAIFI nor Restoration of Supply data during the current regulatory period 2010-2015. Subject to further monitoring and future AER reporting requirements.
Back to Index

## TSD_014
Upper North/Eyre Peninsula Region Reliability Performance
From 2015-16, SA Power Networks is not measured on performance in individual regions. Referto OP 2.1 and OP 2.3 for overall regional monitoring.
Performance Measure | TARGET | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
SAIDI | 370 | 399 | 293 | 341 | 303 | 399 | 610 | 481 | 361 | 375 | 632
SAIFI | 2.5 | 3.37 | 2.9 | 2.24 | 2.1 | 2.71 | 3.31 | 2.3 | 1.99 | 2.49 | 2.52
CAIDI (Implied target) | 150 | 118 | 101 | 153 | 144 | 147 | 184 | 209 | 181 | 150 | 251
MAIFI (frequency)(1) | N/A | N/A | N/A | N/A | N/A | N/A | 2.16 | 3.18 | 0.8 | 2.4 | 11.29
Restoration of Supply | 80% within 4h | 84% | 85% | 70% | 80% | 81% | 77% | 79% | 77% | 82% | 65%
Restoration of Supply | 90% within 6h | 90% | 95% | 88% | 90% | 95% | 89% | 83% | 87% | 94% | 81%
Annual SAIDI Severe Weather Events (min)(2) | - | - | - | - | - | - | - | 151.6 | 171.7 | 131.2 | 311.8
(1) Momentary Interruptions per Customer (MAIFI) means the total number of momentary interruptions (of less than 60 seconds duration) divided by the number of customers.
(2) A Severe Weather Event is defined as a weather related event where the contribution to regional SAIDI was the greater of three (3) minutes, or three (3) per cent of the Regional SAIDI standard in clause 1.1.3.1 of the Electricity Distribution Code.
2010-15 TARGETS
Performance Measure |  | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
SAIDI | 425 | 840.8 | 381.8 | 474.4 | 390.1 | 353.8
SAIFI | 2.3 | 2.722 | 1.711 | 1.61 | 1.691 | 1.432
CAIDI (Implied target) | N/A | 308.8905 | 223.1444 | 294.6584 | 230.6919 | 247.067
Annual SAIDI Severe Weather Events (min) | - | 523.3 | 74.5 | 217.9 | 90.3 | 26.8
The Commission is not collecting MAIFI data during the current regulatory period 2010-2015. Subject to further monitoring and future AER reporting requirements.
Back to Index

## TSD_015
South East Region Reliability Performance
From 2015-16, SA Power Networks is not measured on performance in individual regions. Referto OP 2.1 and OP 2.3 for overall regional monitoring.
Performance Measure | TARGET | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
SAIDI | 330 | 524 | 277 | 347 | 345 | 230 | 256 | 489 | 328 | 226 | 278
SAIFI | 2.7 | 3.61 | 2.06 | 2.07 | 2.08 | 2.35 | 2.36 | 3.78 | 2.65 | 1.86 | 2.54
CAIDI (Implied target) | 120 | 145 | 135 | 168 | 166 | 98 | 109 | 129 | 124 | 121 | 109
MAIFI (frequency)(1) | N/A | N/A | N/A | N/A | N/A | N/A | 3.94 | 5.09 | 3.3 | 2.4 | 4.81
Restoration of Supply | 80% within 4h | 84% | 85% | 70% | 80% | 81% | 77% | 79% | 90% | 92% | 92%
Restoration of Supply | 90% within 5h | 90% | 95% | 88% | 90% | 95% | 89% | 83% | 94% | 95% | 95%
Annual SAIDI Severe Weather Events (min)(2) | - | - | - | - | - | - | - | 108.5 | 20.3 | 25.9 | 10.9
(1) Momentary Interruptions per Customer (MAIFI) means the total number of momentary interruptions (of less than 60 seconds duration) divided by the number of customers.
(2) A Severe Weather Event is defined as a weather related event where the contribution to regional SAIDI was the greater of three (3) minutes, or three (3) per cent of the Regional SAIDI standard in clause 1.1.3.1 of the Electricity Distribution Code.
2010-15 TARGETS
Performance Measure |  | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
SAIDI | 295 | 277.1 | 243.8 | 411.4 | 427.5 | 198.9
SAIFI | 2.5 | 1.665 | 2.012 | 2.56 | 2.445 | 1.667
CAIDI (Implied target) | N/A | 166.4264 | 121.173 | 160.7031 | 174.8466 | 119.3161
Annual SAIDI Severe Weather Events (min) | - | 151 | 11 | 202.5 | 108.3 | 4
The Commission is not collecting MAIFI data during the current regulatory period 2010-2015. Subject to further monitoring and future AER reporting requirements.
Back to Index

## TSD_016
Kangaroo Island Region Reliability Performance
From 2015-16, SA Power Networks is not measured on performance in individual regions. Referto OP 2.1 and OP 2.3 for overall regional monitoring.
Performance Measure | TARGET | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
SAIDI | 450 | 932 | 1084 | 905 | 1960 | 290 | 1354 | 510 | 565 | 232 | 371
SAIFI | N/A | 3.83 | 9.83 | 8.93 | 13.74 | 3.04 | 9.34 | 7.33 | 7.85 | 2.95 | 4.89
CAIDI | N/A | 243 | 110 | 101 | 101 | 96 | 145 | 70 | 72 | 79 | 76
MAIFI (frequency)(1) | N/A | N/A | N/A | N/A | N/A | N/A | 3.05 | 0 | 2.6 | 3.6 | 4.98
Restoration of Supply | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Annual SAIDI Severe Weather Events (min)(2) | - | - | - | - | - | - | - | 19 | 271.1 | 45.4 | 134.8
(1) Momentary Interruptions per Customer (MAIFI) means the total number of momentary interruptions (of less than 60 seconds duration) divided by the number of customers.
(2) A Severe Weather Event is defined as a weather related event where the contribution to regional SAIDI was the greater of three (3) minutes, or three (3) per cent of the Regional SAIDI standard in clause 1.1.3.1 of the Electricity Distribution Code.
2010-15 TARGETS
Performance Measure |  | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
SAIDI | 450 | 197.9 | 336.7 | 686.6 | 384.9 | 266.4
SAIFI | N/A | 2.448 | 2.346 | 3.97 | 2.851 | 3.177
CAIDI (Implied target) | N/A | 80.8415 | 143.5209 | 172.9471 | 135.0053 | 83.8527
Annual SAIDI Severe Weather Events (min) | - | 84.6 | 95.7 | 329.6 | 78.5 | 5.8
The Commission is not collecting MAIFI data during the current regulatory period 2010-2015. Subject to further monitoring and future AER reporting requirements.
Back to Index

## TSD_017
Quality of Supply (previously OP 3.1) Quality of Supply is monitored under the National Energy Customer Framework (NECF) from 2015.
DETAIL | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
Number of customer enquiries | 659 | 863 | 1104 | 1381 | 1727 | 1541 | 1384 | 1380 | 1911 | 2186 | 2173 | 2086 | 2255 | 2197 | 2034
Customers not advised of result within 20 business days | 413 | 378 | 274 | 316 | 194 | 226 | 163 | 197 | 282 | 246 | 149 | 211 | 261 | 165 | 126
Number of customers requiring changes to network supply arrangements | 443 | 509 | 463 | 554 | 872 | 764 | 528 | 541 | 481 | 621 | 441 | 430 | 549 | 323 | 470
Number of customers requiring changes to network supply arrangements, not completed within 60 days | 19 | 376 | 398 | 420 | 380 | 251 | 160 | 132 | 137 | 109 | 24 | 27 | 62 | 39 | 0
Back to Index

## TSD_018
SA Power Networks’ Customer Compensation payments for Quality of Service (voltage variation) previously OP 3.2 . Quality of Service is monitored under the National Energy Customer Framework (NECF) from 2015.
DETAIL | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
Number of customer compensation events(1) | 174 | 102 | 189 | 130 | 169 | 134 | 129 | 132 | 128 | 445 | 362 | 176
Total paid | 281685 | 219407 | 355422 | 193656 | 503166 | 154251 | 307151 | 235337 | 482772 | 512161 | 398299 | 261943
Minimum amount paid per customer compensation event | 15 | 22 | 30 | 35 | 28 | 40 | 53 | 46 | 25 | 16 | 32 | 47
Maximum amount paid per customer compensation event | 93427 | 44245 | 91382 | 99581 | 85434 | 7866 | 105314 | 43508 | 163394 | 13500 | 11240 | 6735
(1) A voltage variation event can impact on more than one customer. A compensation event is defined as a network event that results in a breach of power quality standards and results in some damage to customer equipment.
Back to Index

## TSD_019
Back to Index | OP 3.1 - SA Power Networks’ Performance Against Timeliness of Appointments
| Measure | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
| Number of appointments | 17959 | 23217 | 24897 | 24388 | 23400 | 23408 | 22972 | 26813 | 30340 | 32995 | 53338 | 84111 | 52077 | 45931 | 31973 | 30214 | 32369 | 29279 | 20666 | 21290
| Number of appointments where SA Power Networks is more than 15 minutes late | 24 | 29 | 28 | 15 | 4 | 14 | 12 | 13 | 13 | 2 | 3 | 0 | 0 | 1 | 0 | 2 | 1 | 2 | 1 | 1
| Percentage of appointments where SA Power Networks is not more than 15 minutes late | 99.9% | 99.9% | 99.9% | 99.9% | 99.98% | 99.9% | 99.95% | 99.95% | 99.96% | 99.99% | 99.99% | 100% | 100% | 99.99% | 100% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99%
| Amounts paid to customers where SA Power Networks is more than 15 minutes late | 400 | 580 | 560 | 300 | 80 | 280 | 240 | 260 | 260 | 40 | 90 | 0 | 0 | 25 | 0 | 50 | 25 | 50 | 25 | 25
Back to Index

## TSD_020
OP 4.2 - SA Power Networks’ Performance Against Promptness of Connection
Measure | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Number of new supply addresses connected | 7270 | 9106 | 10702 | 12973 | 12802 | 13423 | 13052 | 13033 | 14933 | 13853 | 14187 | 11585 | 9480 | 10721 | 11901 | 11620 | 11805 | 11789 | 10016 | 9541
Number of new supply addresses not connected within the prescribed period | 134 | 143 | 173 | 160 | 117 | 179 | 67 | 172 | 87 | 88 | 82 | 77 | 65 | 121 | 141 | 192 | 238 | 215 | 229 | 182
Percentage of new supply addresses connected within the prescribed period | 98.16% | 98.43% | 98.38% | 98.77% | 99.09% | 98.67% | 99.49% | 98.68% | 99.42% | 99.36% | 99.42% | 99.34% | 99.31% | 98.87% | 98.82% | 98.35% | 97.98% | 98% | 97.7% | 98.1%
Amounts paid to customers where SA Power Networks failed to connect new supply addresses within the prescribed period | 13550 | 15785 | 15000 | 21500 | 24550 | 16000 | 15150 | 41100 | 17950 | 17150 | 18480 | 19860 | 14560 | 30840 | 37620 | 52620 | 71930 | 60975 | 64610 | 70320
Back to Index

## TSD_021
OP 4.3 - SA Power Networks’ Performance Against Timeliness of Street Light Repairs – Adelaide Business Area and Major Metropolitan Areas
Measure | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
No. street light faults reported/repaired (from 2010/11) | 33254 | 42307 | 29309 | 27640 | 32560 | 29320 | 31829 | 31450 | 24268 | 31439 | 25090 | 25735 | 22669 | 25648 | 26782 | 27486 | 35181 | 26589 | 26044 | 24130
No. street light faults not repaired within 5 business days | 682 | 2202 | 1597 | 1974 | 1654 | 1895 | 841 | 609 | 315 | 1159 | 1763 | 1055 | 1361 | 906 | 1795 | 1126 | 3726 | 1022 | 1403 | 1690
% of street light faults repaired within 5 business days | 97.95% | 94.8% | 94.55% | 92.86% | 94.92% | 93.54% | 97.36% | 98.06% | 98.7% | 96.31% | 92.97% | 95.9% | 94% | 96.47% | 93.3% | 95.9% | 89% | 96% | 95% | 93%
Average no. business days to repair street light faults | N/A | N/A | 3 | 4 | 4 | 3.5 | 2.3 | 3 | 2 | 2.5 | 3.4 | 3.4 | 2.6 | 3.66 | 4.83 | - | - | - | - | -
Customer payments where SA Power Networks failed to effect repairs within 5 business days | 27530 | 92800 | 42060 | 88400 | 74220 | 142760 | 31620 | 31080 | 15420 | 28260 | 72565 | 43725 | 73830 | 71975 | 255400 | 190650 | 442600 | 154585 | 149435 | 252625
Back to Index

## TSD_022
OP 4.4 - SA Power Networks’ Performance Against Timeliness of Street Light Repairs – Country Areas
Measure | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
No. street light faults reported/repaired (from 2010/11) | 12024 | 7836 | 5833 | 5446 | 7101 | 7088 | 6220 | 5455 | 4213 | 5453 | 3947 | 3696 | 3441 | 3657 | 3867 | 4149 | 5212 | 4356 | 4147 | 3322
No. street light faults not repaired within 10 business days | 289 | 107 | 59 | 118 | 133 | 100 | 159 | 37 | 25 | 79 | 159 | 60 | 67 | 26 | 27 | 12 | 53 | 23 | 52 | 44
% of street light faults reported repaired within 10 business days | 97.6% | 98.63% | 98.99% | 97.83% | 98.13% | 98.59% | 97.44% | 99.32% | 99.41% | 98.55% | 95.97% | 98.38% | 98.05% | 99.29% | 99.3% | 99.71% | 99% | 99% | 99% | 99%
Average no. business days to repair street light faults | N/A | N/A | 4 | 4 | 3.1 | 4 | 4 | 3 | 3.5 | 4 | 4 | 4.5 | 3.25 | 3.1 | - | - | - | - | - | -
Customer payments where SA Power Networks failed to effect repairs within 10 business days | 3200 | 1280 | 1200 | 2700 | 2660 | 2780 | 2840 | 1040 | 600 | 1460 | 2890 | 1250 | 1625 | 800 | 1575 | 425 | 2150 | 1950 | 2950 | 4000
Back to Index

## TSD_023
OP 4.5 - GSL: Frequency of Supply Interruptions
DETAIL | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Frequency of supply >9 and ≤12 interruptions | 3549 | 1041 | 559 | 911 | 2288 | 2653 | 1164 | 1142 | 3258 | 779 | 395 | 3194 | 525 | 290 | 363
Payment total | 283920 | 83280 | 44720 | 72880 | 183040 | 238770 | 104760 | 102780 | 293220 | 70110 | 39500 | 319400 | 52500 | 29000 | 36300
Frequency of supply >12 and ≤15 interruptions | 827 | 426 | 215 | 179 | 1269 | 402 | 883 | 23 | 368 | 58 | 74 | 724 | 19 | 37 | 28
Payment total | 99240 | 51120 | 25800 | 21480 | 127520 | 56280 | 123620 | 3220 | 51520 | 8120 | 11100 | 108600 | 2850 | 5550 | 4200
Frequency of supply >15 interruptions | 70 | 63 | 2 | 0 | 405 | 62 | 0 | 0 | 3 | 12 | 0 | 14 | 0 | 0 | 0
Payment total | 11200 | 10080 | 320 | 0 | 64240 | 11470 | 0 | 0 | 555 | 2220 | 0 | 2800 | 0 | 0 | 0
Back to Index

## TSD_024
OP 4.6 - GSL: Duration of Supply Interruptions
DETAIL | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Duration of supply interruption >12 and ≤15h | 2177 | 2269 | 1379 | 1907 | 3218 | 9980 | 2821 | 6540 | 15235 | 3477 | 2946 | 33711 | 2898 | 8888 | 2519
Payment total | 174160 | 181600 | 110320 | 152560 | 257440 | 888980 | 253870 | 588680 | 1371150 | 312930 | 592501 | 3371100 | 289800 | 1090500 | 251900
Duration of supply interruption >15 and ≤18h | 1993 | 896 | 753 | 1065 | 3208 | 7274 | 2917 | 2765 | 9829 | 2870 | 3630 | 25830 | 2211 | 5197 | 3257
Payment total | 239160 | 107520 | 90360 | 127800 | 384960 | 1017700 | 408320 | 387100 | 1376060 | 401800 | 544500 | 3874500 | 331650 | 1333200 | 488550
Duration of supply interruption >18 and ≤24h | 6070 | 1189 | 444 | 694 | 1932 | 8121 | 3923 | 6405 | 14457 | 3369 | 3051 | 30048 | 1117 | 1427 | 4200
Payment total | 971200 | 190240 | 71040 | 111040 | 309120 | 1502185 | 725705 | 1184925 | 2674545 | 623265 | 610200 | 6009600 | 223400 | 1039400 | 840000
Duration of supply interruption >24h |  | 292 | 281 | 123 | 620 | 8803 | 2520 | 2513 | 9310 | 2793
Payment total |  | 93440 | 89920 | 39360 | 198400 | 3253510 | 932400 | 930130 | 3444700 | 1033410
Duration of supply interruption >24h and ≤48h | [10 empty] | 1049 | 23576 | 460 | 1427 | 1453
Payment total | [10 empty] | 424845 | 9548280 | 186300 | 577935 | 588465
Duration of supply interruption >48h | [10 empty] | 52 | 7744 | 68 | 45 | 19
Payment total | [10 empty] | 31460 | 4685120 | 41140 | 27225 | 11495
TOTAL | 1384520 | 572800 | 361640 | 430760 | 1149920 | 6662375 | 2320295 | 3090835 | 8866455 | 2371405 | 2203506 | 27488600 | 1072290 | 4068260 | 2180410
Back to Index

## TSD_025
OP 6.1 - SA Power Networks’ Network Energy Losses
Measure | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2012/14 | 2014/15
Energy Delivered to Network (GWh) | 11043 | 10737 | 11073 | 11153 | 11186 | 11678 | 11973 | 12048 | 12042 | 12162 | 11959 | 11700 | 11702 | 11340 | 11035.24
Energy Delivered to Customers (GWh) | 10316 | 10091 | 10446 | 10689 | 10276 | 10829 | 11299 | 11380 | 11269 | 11457 | 11236 | 10995 | 11003 | 10663 | 10359.108
Distribution Network Losses (%) | 6.583% | 6.017% | 5.662% | 4.16% | 8.135% | 7.27% | 5.629% | 5.544% | 6.419% | 5.797% | 6.046% | 6.026% | 5.973% | 5.97% | 6.127%
Losses Reported 00/01 to 06/07 (error) | 7.047% | 6.402% | 6.002% | 4.341% | 8.856% | 7.84% | 5.965%
Back to Index

## TSD_026
Distribution Code Reliability Performance Targets, Measured Overall Performance of SA Power Networks (CAIDI - Minutes)(1)
Region | IMPLIED TARGET | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
Adelaide Business Area | 80 | 73 | 122 | 71 | 108 | 86 | 53 | 88 | 125 | 123 | 50
Major Metropolitan Areas | 82 | 83 | 79 | 78 | 81 | 82 | 89 | 80 | 89 | 94 | 94
Central | 115 | 104 | 113 | 144 | 108 | 122 | 146 | 132 | 136 | 122 | 148
Eastern Hills & Fleurieu Peninsula | 105 | 118 | 97 | 111 | 104 | 112 | 111 | 147 | 106 | 105 | 126
Upper North & Eyre Peninsula | 150 | 118 | 101 | 153 | 144 | 147 | 184 | 209 | 181 | 150 | 251
South East | 120 | 145 | 135 | 168 | 166 | 98 | 109 | 129 | 124 | 121 | 109
Kangaroo Island | N/A | 243 | 110 | 101 | 101 | 96 | 145 | 70 | 72 | 79 | 76
Total (State-wide) | 97 | 97 | 90 | 100 | 97 | 99 | 107 | 105 | 104 | 105 | 117
Note 1: SA Power Networks is not required to report CAIDI performance in the current Service Standards for 2010-2015
Back to Index

## TSD_027
SA Power Networks’ performance against Time to Restore Supply service standards,(1) Distribution Code
Region | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
ABA - 90% of customers restored within 2 hours | 94% | 59% | 95% | 93% | 71% | 92% | 89% | 37% | 65% | 99%
ABA - 95% of customers restored within 3 hours | 96% | 93% | 97% | 100% | 95% | 100% | 99% | 100% | 69% | 99%
MMA - 80% of customers restored within 2 hours | 78% | 83% | 84% | 83% | 81% | 78% | 83% | 81% | 73% | 76%
MMA - 90% of customers restored within 3 hours | 91% | 94% | 95% | 84% | 92% | 92% | 94% | 94% | 92% | 90%
CEN - 80% of customers restored within 3 hours | 87% | 83% | 73% | 86% | 79% | 77% | 77% | 75% | 82% | 75%
CEN - 90% of customers restored within 5 hours | 97% | 95% | 89% | 97% | 92% | 92% | 91% | 93% | 94% | 89%
EHFP - 80% of customers restored within 3 hours | 79% | 91% | 82% | 88% | 87% | 90% | 75% | 83% | 87% | 79%
EHFP - 90% of customers restored within 4 hours | 90% | 97% | 93% | 92% | 92% | 93% | 83% | 92% | 91% | 90%
UNEP - 80% of customers restored within 4 hours | 84% | 85% | 70% | 80% | 81% | 77% | 79% | 77% | 82% | 65%
UNEP - 90% of customers restored within 6 hours | 90% | 95% | 88% | 90% | 95% | 89% | 83% | 87% | 94% | 81%
SE - 80% of customers restored within 4 hours | 92% | 92% | 90% | 83% | 95% | 92% | 88% | 90% | 92% | 92%
SE - 90% of customers restored within 5 hours | 90% | 98% | 92% | 88% | 98% | 94% | 96% | 94% | 95% | 95%
KI - Performance Standard Not Applicable | - | - | - | - | - | - | - | - | - | -
ABA = Adelaide Business Area; MMA = Major Metropolitan Areas; CEN = Central; EHFP = Eastern Hills & Fleurieu Peninsula, UNEP = Upper North & Eyre Peninsula; SE = South-East; KI = Kangaroo Island
Note 1: SA Power Networks is not required to report restoration performance in the current Service Standards for 2010-2015.
Back to Index

## TSD_028
Summary - Performance against Guaranteed Service Levels (Customer Payments)
Requirement | 2000/01 | 2001/02 | 2002/03 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20
Timeliness of appointments - No more than 15 minutes late | 400 | 580 | 560 | 300 | 80 | 280 | 240 | 260 | 260 | 40 | 90 | 0 | 0 | 25 | 0 | 50 | 25 | 50 | 25 | 0
Promptness of new connections - Within 6 business days | 13550 | 15785 | 15000 | 21500 | 24550 | 16000 | 15150 | 41100 | 17950 | 17150 | 18480 | 19860 | 14560 | 30840 | 37620 | 37620 | 71930 | 60975 | 64100 | 70320
Timeliness of street light repairs - Metro/Other - Within 5 business days | 27530 | 92800 | 42060 | 88400 | 74220 | 142760 | 31620 | 31080 | 15420 | 28260 | 72565 | 43725 | 73830 | 71975 | 255400 | 255400 | 442600 | 154585 | 149435 | 252625
Timeliness of street light repairs - Country - Within 10 business days | 3200 | 1280 | 1200 | 2700 | 2660 | 2780 | 2840 | 1040 | 600 | 1460 | 2890 | 1250 | 1625 | 800 | 1575 | 1575 | 2150 | 1950 | 2950 | 4000
Duration of supply interruption >12 and ≤15h | N/A | N/A | N/A | N/A | N/A | 174160 | 181600 | 110320 | 152560 | 257440 | 888980 | 253870 | 588680 | 1371150 | 312930 | 312930 | 3371100 | 289800 | 1090500 | 251900
Duration of supply interruption >15 and ≤18h | N/A | N/A | N/A | N/A | N/A | 239160 | 107520 | 90360 | 127800 | 384960 | 1017700 | 408320 | 387100 | 1376060 | 401800 | 401800 | 3874500 | 331650 | 1333200 | 488550
Duration of supply interruption >18 and ≤24h | N/A | N/A | N/A | N/A | N/A | 971200 | 190240 | 71040 | 111040 | 309120 | 1502185 | 725705 | 1184925 | 2674545 | 623265 | 623265 | 6009600 | 223400 | 1039400 | 840000
Duration of supply interruption >24h and ≤48h | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1033410 | 1033410 | 9548280 | 186300 | 577935 | 588465
Duration of supply interruption >48h | 2016/17: 4685120; 2017/18: 41140; 2018/19: 27225; 2019/20: 11495
Frequency of supply >9 and ≤12 interruptions | N/A | N/A | N/A | N/A | N/A | 283920 | 83280 | 44720 | 72880 | 183040 | 238770 | 104760 | 102780 | 293220 | 70110 | 70110 | 319400 | 52500 | 29000 | 36300
Frequency of supply >12 and ≤15 interruptions | N/A | N/A | N/A | N/A | N/A | 99240 | 51120 | 25800 | 21480 | 127520 | 56280 | 123620 | 3220 | 51520 | 8120 | 8120 | 108600 | 2850 | 5550 | 4200
Frequency of supply >15 interruptions | N/A | N/A | N/A | N/A | N/A | 11200 | 10080 | 320 | 0 | 64240 | 11470 | 0 | 0 | 555 | 2220 | 2220 | 2800 | 0 | 0 | 0
| 44680 | 110445 | 58820 | 112900 | 101510 | 1940700 | 673690 | 416040 | 519990 | 1373230 | 3809410 | 1681110 | 2356720 | 5870690 | 2746450 | 2746500 | 28436105 | 1345200 | 4319320 | 2547855
Back to Index

## TSD_030
OP1 – Connection point restoration Standards
OP1(a) (from September 2013) – Connection Point Restoration Standards - Line Failure
Indicator | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20
Number of transmission line failures | 0 | 1 | 1 | 1* | 0 | 0 | 0
OP1(b) (from September 2013) – Connection Point Restoration Standards - Transformer Failure
Indicator | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20
Number of transformer failures | 2 | 0 | 0 | 0 | 0 | 0 | 0
This proforma deleted from 2013 - Requests for information on any interruptions or restrictions to the provision of transmission services (clause 3.4)
Indicator | 98/99 | 99/00 | 00/01 | 01/02 | 02/03 | 03/04 | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14
Total number of requests by a generator, distributor, or transmission customer to provide a written response explaining any interruption or restriction to Transmission services | ─ | ─ | ─ | ─ | ─ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | N/A
Number of requests answered with a written response within ten (10) business days by the Licensee | ─ | ─ | ─ | ─ | ─ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | N/A
Percentage of requests answered with a written response within ten (10) business days by the Licensee | ─ | ─ | ─ | ─ | ─ | ─ | ─ | ─ | ─ | ─ | ─ | ─ | ─ | ─ | 100% | N/A
* Does not include the events of 28th September 2016
Back to Index

## TSD_031
OP2 (from September 2013) – Power System Incidents
Previously OP 2
Indicator | 98/99 | 99/00 | 00/01 | 01/02 | 02/03 | 03/04 | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20
No. of Interruptions | 23 | 27 | 24 | 14 | 32 | 23 | 19 | 26 | 14 | 11 | 13 | 17 | 14 | 14 | 14 | 13 | 7 | 4 | 9* | 6 | 6 | 7
System Minutes Off Supply | 2.4 | 12 | 5 | 1.4 | 4.3 | 2.7 | 2.1 | 0.86 | 1.69 | 0.71 | 1.35 | 3.15 | 2.46 | 8.31 | 5.35 | 5.57 | 0.32 | 0.543 | 13.196* | 1.6 | 1.33 | 2.68
* Does not include the events of 28th September 2016 | bar: 98/99 to 00/01
Back to Index

## TSD_032
OP3 (from September 2013) – Operational Statistics – RELIABILITY (incorporating the information requirements of the Technical Regulator)
Previously OP 4a
Indicator | 98/99 | 99/00 | 00/01 | 01/02 | 02/03 | 03/04 | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20
Interconnector Availability* (%) |  |  |  |  | n/a | 99.73 | 99.36 | 99.43 | 98.4 | 99.89 | 99.76 | 99.97 | 99.57 | 99.7 | 99.9 | 99.97 | 99.99 | 99.998 | 98.967 | 99.937 | 99.296 | 99.99
Transmission Line Availability (%) | 99.25 | 99.29 | 99.32 | 99.3 | 99.38 | 99.59 | 99.54 | 99.27 | 99.41 | 99.34 | 99.38 | 99.75 | 99.42 | 98.64 | 98.68 | 99.34 | 99.52 | 99.174 | 99.559 | 99.38 | 98.916 | 98.72
ElectraNet SA historical performance
INDICATOR | Target | 99/00 | 00/01 | 01/02 | 02/03 | 03/04 | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20
Loss of Supply Event Frequency > 0.2 min | 5-6 | 9 | 5 | 3 | 4 | 2 | 7 | 0 | 4 | 1 | 0 | 4 | 5 | 4 | 7 | 2 | 0 | 3 | 1 | 1 | 3 | 1
Loss of Supply Event Frequency > 1.0 min | 2 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1
Ave. outage duration (minutes) | 100-110 | 70.9 | 141.3 | 108.6 | 70.03 | 70.13 | 48.92 | 110.35 | 88.46 | 270 | 203 | 120.6 | 130.1 | 961 | 122 | 152 | 110 | 450 | 934 | 33 | 173 | 1197
Note on B5: ESCOSA - * Heywood (SA/Vic) Interconnector based on 2 circuits from the SA/Vic border to Para substation
Back to Index

## TSD_033
OP3 (from September 2013) – Operational Statistics – STATISTICAL (incorporating the information requirements of the Technical Regulator)
Previously OP 4b
Indicator | 02/03 | 03/04 | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20
Electricity delivered at transmission exits (MWh) | 12230135 | 12058924 | 12137172 | 12571032 | 13381276 | 13107150 | 13326576 | 13266263 | 13362667 | 12955955 | 12928030 | 12340571 | 12004316.39 | 12325698 | 11817090 | 11749259 | 11629167.93 | 11414491
Circuit length (km) | 5579 | 5579 | 5658 | 5676 | 5676 | 5575 | 5589 | 5591 | 5591 | 5571 | 5560 | 5603 | 5591 | 5617 | 5600 | 5645 | 5680 | 5627
Back to Index

## TSD_034
OP 3 – Operational Statistics - TECHNICAL - (incorporating the information requirements of the Technical Regulator)
Previously OP 4d
Detail | 98/99 | 99/00 | 00/01 | 01/02 | 02/03 | 03/04 | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18 | 18/19 | 19/20
Substation Routine Task Rate | ─ | ─ | ─ | ─ | N/A | 1583 | 2097 | 3272 | 4280 | 3794 | 4335 | 3720 | 3437 | 2708 | 3541 | 4150 | 4104 | 5300 | 4 953 | 5056 | 5343 | 5910
Line Routine Task Rate | ─ | ─ | ─ | ─ | N/A | 438 | 469 | 1309 | 1086 | 1075 | 1117 | 1300 | 1700 | 1612 | 1326 | 1519 | 1557 | 1374 | 1359 | 1690 | 1555 | 1790
Substation Corrective Task Rate | ─ | ─ | ─ | ─ | N/A | 2316 | 2420 | 2393 | 2273 | 1089 | 1707 | 1876 | 1872 | 2708 | 3152 | 3469 | 5046 | 7164 | 5811 | 6288 | 6398 | 7768
Line Corrective Task Rate | ─ | ─ | ─ | ─ | N/A | 931 | 858 | 999 | 1063 | 410 | 1025 | 491 | 265 | 2676 | 2740 | 2105 | 4069 | 4226 | 4836 | 4206 | 7180 | 7791
Vegetation infringements | ─ | ─ | ─ | ─ | ─ | ─ | 1 | ─ | ─ | ─ | ─ | ─ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency Cuts | ─ | ─ | ─ | ─ | N/A | 1 | _ | ─ | ─ | ─ | ─ | ─ | ─ | 0 | 0 | 0 | 0 | - | - | 0 | 0 | 0
Fire Starts | ─ | ─ | ─ | ─ | _ | 7 | 2 | ─ | ─ | ─ | ─ | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Major plant failure events | ─ | ─ | ─ | ─ | 3 | 6 | 3 | 4 | 4 | 5 | 0 | 2 | 3 | 5 | 3 | 6 | 9 | 7 | 0 | 4 | 0 | 0
Plant related safety events | ─ | ─ | ─ | ─ | 3 | 1 | 3 | 6 | 1 | 1 | 1 | 2 | 2 | 6 | 3 | 4 | 5 | 3 | 11 | 6 | 13 | 10
Electric shock reports | ─ | ─ | ─ | ─ | 1 | ─ | 1 | ─ | ─ | ─ | ─ | ─ | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1
Switching incident rate % | ─ | ─ | ─ | ─ | 0.14% | 0% | 0% | 0.35% | 0.28% | 0.28% | 0.86% | 0.74% | 0.56% | 0.26% | 0.3% | 0.3% | 0.11% | 0.08% | 0.16% | 0.26% | 0.45% | 0.08%
Note on C10: ESCOSA- to be defined by OTR & ElectraNet
Back to Index
Back to Index

## TSD_035
Interconnector Import/Export Details (1)
Detail | 98/99 | 99/00 | 00/01 | 01/02 | 02/03 | 03/04 | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16
Heywood - Import GWh | ─ | 3574 | 2471 | 1439 | 2191 | 2554 | 2214 | 2374 | 1245.8 | 657 | 822.8 | 1104.5 | 1155.2 | 1490 | 1632 | 1822 | 1949 | 2013
Heywood - Export GWh | ─ | 1 | 18 | 123 | 54 | 31 | 59 | 35 | 234.7 | 525.6 | 429.3 | 299.2 | 364.2 | 241 | 239 | 181 | 204 | 172
Murraylink – Import GWh | ─ | ─ | ─ | ─ | 206 | ─ | ─ | 270 | 86.8 | 40.1 | 51.5 | 78.5 | 79.2 | 134 | 155 | 189 | 142 | 320
Murraylink - Export (GWh) | ─ | ─ | ─ | ─ | 10 | ─ | ─ | 31 | 155.7 | 175.9 | 217.3 | 265.8 | 303.9 | 246 | 143 | 157 | 297 | 220
(1) Refer AEMO web site; www.aemo.com.au
Back to Index

## TSD_036
OP4 (from September 2013) – Exit Point Demand Forecasts
Indicator | 98/99 | 99/00 | 00/01 | 01/02 | 02/03 | 03/04 | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13
Agreed Maximum Demand (MW) | ─ | ─ | ─ | ─ | 3127.456 | 3127.456 | 3231.289 | 3310.18 | 3364.456 | 3440.213 | 3540.985 | 3733.185 | 3818.085 | 3910.008 | 3946.008
Forecast Agreed Maximum Demand (MW) 3 year forward demand forecasts | 98/99: 13/14; 99/00: Year 2; 00/01: Year 3
| 3646.55 | 3626.05 | 3626.85
|  | 14/15 | Year 2 | Year 3
|  | 3613 | 3612 | 3613
|  |  | 15/16 | Year 2 | Year 3
|  |  | 3608 | 3608 | 3580
Back to Index

## TSD_040
Promptness of connection - Discontinued. From 2013, customer service provisions are captured under the national framework (NECF)
Detail | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14
Total number of new supply addresses connected | 7456 | 8728 | 8576 | 8751 | 8850 | 8800 | 9834 | 8459 | 7781
Total number of new supply addresses not connected by licensee on a date agreed with the customer, or where no date has been agreed with the customer, within 20 business days after the necessary pre-conditions have been met | <20 | <20 | <20 | <20 | <20 | <20 | <20 | 4 | 13
Total number of previously connected supply addresses re-connected | 4371 | 5333 | 5211 | 6074 | 7212 | 4986 | 3992 | 5265 | 2817
Total number of previously connected supply addresses not connected by licensee within one business day of receiving notification from the retailer and after the necessary pre-conditions have been met | <12 | <12 | <12 | <12 | <12 | <12 | <12 | 85 | 57
Back to Index

## TSD_041
Network Extension and Expansion Charges - Discontinued from 2013. The Commisson is no longer responsible for costs associated with gas connections
Detail | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14
Number of network extension and expansion projects approved during period | 452 | 382 | 386 | 392 | 231 | 230 | 246 | 263 | 218
Number of network extensions and expansions approved involving a customer contribution | 44 | 67 | 45 | 37 | 113 | 132 | 104 | 79 | 74
Amount ($) charged to customers during the period for network extensions and expansions | 59436 | 71816 | 41702 | 67108 | 312848 | 326900 | 216000 | 126200 | 208900
Back to Index

## TSD_042
Number of Interruptions - Discontinued from 2013. Interruption data is now captured within the NECF
Detail | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13
Number of Planned Interruptions (clause 6.1.1) | 3068 | 4487 | 4209 | 5568 | 2817 | 4372 | 6127 | 7343 | 7087
Number of metering installations replaced (clause 6.2.1) | ─ | ─ | 31539 | 42381 | 34491 | 37263 | 24863 | 20891 | 22251
Number of customers requesting relight service following replacement of metering installation (clause 6.2.1) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 416 | 460
Number of Unplanned Interruptions* | 4 | 10 | 31 | 51 | 70 | 66 | 69 | 2624 | 2545
* Including Major Interruptions and domestic service damages.
Back to Index

## TSD_043
OP1 (from September 2013) Major Interruptions
Detail | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18
Total Number of Major Interruptions | 3 | 9 | 7 | 13 | 2 | 22 | 5 | 20 | 11 | 17 | 15 | 20 | N/A | N/A
Total Number of Customers affected | 815 | 339 | 387 | 3664 | 60 | 352 | 66 | 3881 | 1111 | 409 | 10019 | 619 | N/A | N/A
Duration (customer minutes) | 1420 | 1571 | 4736 | 3689 | 1170 | 6493 | 3258 | 19404 | 3285 | 5265 | 16630 | 7205 | N/A | N/A
Back to Index

## TSD_044
OP 2 (from September 2013) Statistical Information Table (a) and Table (g)
Table (a) Gas entering distribution system (Tj)
Transmission Pipeline | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18
Moomba | 23120 | 27696 | 18626 | 15027 | 17193 | 19037 | 16421 | 13720 | 9609 | 10747 | 14063 | 11997 | 14577 | 17757
South-East | 456 | 2662 | 472 | 438 | 467 | 497 | 542 | 452 | 423 | 454 | 435 | 408 | 453 | 457
SEAGas | 5494 | 8559 | 9585 | 12321 | 10310 | 7787 | 11062 | 12743 | 15768 | 13668 | 9829 | 11069 | 9040 | 5054
Subtotal | 29070 | 38917 | 28683 | 27786 | 27970 | 27321 | 28025 | 26915 | 25800 | 24869 | 24327 | 23474 | 24070 | 23268
Farmtaps | 8913 |  | 9729 | 9934 | 10033 | 9604 | 9698 | 8558 | 8329 | 8986 | 8217 | 8681 | 8078 | 8787
TOTAL | 37983 | 38917 | 38412 | 37720 | 38003 | 36925 | 37723 | 35473 | 34129 | 33855 | 32544 | 32155 | 32148 | 32055
Table (g) Gas distributed to customers
Customer type | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18
Domestic, Industrial & Commercial < 10Tj | 10420 | 11409 | 10417 | 10209 | 10864 | 10635 | 11431 | 10346 | 10461 | 9876 | 10812 | 10312 | 11068 | 10401
Industrial and Commercial ≥ 10Tj | 17131 | 25655 | 16108 | 15816 | 14734 | 14367 | 14567 | 14328 | 14146 | 13282 | 12163 | 11845 | 11947 | 11534
Farm taps | 8913 |  | 9729 | 9934 | 10033 | 9604 | 9698 | 8558 | 8329 | 12 | 8217 | 8681 | 8078 | 8787
TOTAL | 36464 | 37064 | 36254 | 35959 | 35631 | 34606 | 35696 | 33232 | 32936 | 23170 | 31192 | 30838 | 31093 | 30722
Customer type | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18
Domestic, Industrial & Commercial < 10Tj |  | 360565 | 367331 | 374239 | 381106 | 388021 | 395110 | 403301 | 417052 | 423295 | 430094 | 435791 | 441772 | 448093
Industrial and Commercial ≥ 10Tj |  | 169 | 184 | 172 | 168 | 177 | 175 | 173 | 160 | 156 | 139 | 136 | 132 | 128
Farm taps | [5 empty] | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 9 | 9
TOTAL | 0 | 360734 | 367515 | 374411 | 381274 | 388210 | 395297 | 403486 | 417224 | 423463 | 1352 | 1317
UAFG Theoretical not incl farmtaps | 5.225% | 4.761% | 7.524% | 6.338% | 8.481% | 8.488% | 7.233% | 8.326% | 4.624% | 6.88% | 5.558% | 5.61%
UAFG Theoretical total gas | 3.999% | 4.761% | 5.618% | 4.669% | 6.242% | 6.28% | 5.373% | 6.317% | 3.496% | 31.56% | 4.154% | 4.096%
Back to Index

## TSD_045
OP 3 (from September 2013) Technical Information - Table (f) Other Technical Information
Previously OP 6
Performance Indicator | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18
Number of over-pressurisations | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 1 | 3 | 0 | 1 | 0 | N/A | N/A
Number of instances of third party damage (mains and services) | ─ | 778 | 888 | 928 | 948 | 924 | 796 | 714 | 741 | 667 | 672 | 413 | N/A | N/A
Number of locations provided to third parties | ─ | 19923 | 15442 | 20309 | 23225 | 28946 | 33718 | 33639 | 34755 | 33609 | 41189 | 65638 | N/A | N/A
Number of instances where gas enters a building from a mains or inlet leak | 1 | 0 | 0 | 2 | 4 | 4 | 5 | 5 | 2 | 2 | 0 | 4 | N/A | N/A
Number of fires sourced by a gas leak from the network | 0 | 1 | 1 | 0 | 1 | 4 | 0 | 2 | 2 | 3 | 1 | 0 | N/A | N/A
Number of instances and average duration of out of specification gas entering the network (including out of specification odorising level) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
Number of publicly reported leaks (mains and inlets, excluding 3rd party damage above) | 3392 | 2432 | 2515 | 1801 | 1460 | 1514 | 1784 | 1555 | 1505 | 2202 | 2042 | 2272 | N/A | N/A
Number of publicly reported leaks where no leak was found | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1383 | 1319 | 1815 | 1687 | 1725 | N/A | N/A
Number of leaks detected by Leakage Surveys per km of surveyed mains | 0.56 | 0.52 | 0.85 | 0.55 | 0.42 | 0.35 | 0.28 | 0.2 | 0.09 | 0.08 | 0.15 | 0.07 | N/A | N/A
Number of regulator failures (including active) per year | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | N/A | N/A
Number of evacuations (CBD or other) directly attributed to a gas leak from mains or inlet | 0 | 1 | 0 | 2 | 2 | 3 | 4 | 23 | 1 | 2 | 1 | 1 | N/A | N/A
Number of incidents involving attendance of the Fire Brigade and/or emergency services related to a gas leak | 93 | 78 | 70 | 70 | 69 | 111 | 113 | 84 | 6 | 6 | 3 | 3 | N/A | N/A
Number of training hours per SA operations employee/contractor | ─ | 17 | 10.75 | 12 | 9 | 13 | 9 | 10 | 13.5 | 11.91 | 10.58 | 13 | N/A | N/A
Number of completed emergency exercises | ─ | 5 | 5 | 4 | 5 | 2 | 5 | 6 | 5 | 7 | 5 | 7 | N/A | N/A
Number of incidents of stolen gas | 9 | 100 | 128 | 27 | 76 | 54 | 82 | 38 | 112 | 458 | 3 | 3 | N/A | N/A
Back to Index

## TSD_046
OP 4 (from September 2013) Unaccounted for Gas and Mains Replacement Program (As Reported)
Previously OP 7
LEVEL OF UNACCOUNTED FOR GAS - Level of unaccounted for gas determined by AEMO*(monthly)
Detail | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17 | 17/18
Adelaide Metro Network (Tj) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1702 | 1437 | 1297 | 1182.2 | 1098 | 1055 | 1333
Mt Gambier Network (Tj) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 31 | 24 | 26.5 | 23.6 | 16 | N/A | N/A
Other networks Network (Tj) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11 | 21 | 7.4 | 6.8 | 0 | N/A | N/A
TOTAL (Tj) | 1485 | 1680 | 1940 | 1917 | 2153 | 2133 | 1805 | 1744 | 1482 | 1330.9 | 1212.6 | 1114 | 1055 | 1333
* Unaccounted for gas must be reported using unadjusted data provided under the AEMO methodology, as at the end of the relevant reporting period.
^ Unaccounted for gas 2004/05 to 2009/10 as reported by Technical Regulator
RECONCILED LEVEL OF UNACCOUNTED FOR GAS DETERMINED BY AEMO** (ANNUALLY)
Detail | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17
Originally Reported (Tj) | 1744 | 1482 | 1331 | 1213 | 827
Revised (Tj) | 1837 | 1613 | 1435 | 1246
Variance (Tj) | 5.333% | 8.839% | 7.814% | 2.721%
** Envestra must provide updated historical unaccounted for gas data using unadjusted data provided under the AEMO methodology at the conclusion of the 425 day reconciliation process undertaken by AEMO.
|  |  | 0.92753 | 0.072474
MAINS REPLACEMENT - TOTAL
Detail | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17
Total CI and unprotected steel mains replaced | 86 | 75 | 102 | 65 | 87 | 109 | 145.5 | 151.2 | 194.141 | 176.9
MAINS REPLACEMENT PLAN
ADELAIDE METRO
Cast iron and unprotected steel mains replaced | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17
Planned (km) | 113 | 178.8 | 153.6 | 165.7 | 148
Actual (km) | 141.5 | 145.2 | 185.082 | 153.9 | 145
Total mains replaced | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 15/16
Planned (km) | 130 | 205 | 222.3 | 216.2 | 205
Actual (km) | 161.5 | 195.2 | 257.175 | 232.6 | 181
CBD
Cast iron and unprotected steel mains replaced | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17
Planned (km) | 0 | 15.8 | 14.5 | 12.1 | 11.2
Actual (km) | 0 | 0.7 | 3.512 | 13.2 | 11.3
Total mains replaced | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17
Planned (km) | 0 | 18.1 | 16.7 | 18 | 18.1
Actual (km) | 0 | 0.7 | 6.24 | 17.6 | 14.3
MT GAMBIER
Cast iron and unprotected steel mains replaced | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17
Planned (km) | 6.2 | 10.1 | 9 | 8.7 | 5.6
Actual (km) | 4.4 | 5.2 | 5.547 | 9.8 | 5.7
Total mains replaced | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17
Planned (km) | 10.1 | 10.1 | 10 | 22 | 10.1
Actual (km) | 4.4 | 5.2 | 5.547 | 15.6 | 6.7
Back to Index

## TSD_047
OP 5 (from September 2013) Total Number of Complaints (Ombudsman and Direct contact)
Complaint | Ombudsman Complaints | [11 empty] | Direct Complaints
| 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 13/14 | 14/15 | 15/16 | 16/17
Detectability of gas by odour | 2 | ─ | ─ | 2 | 1 | ─ | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | ─ | 1 | 1 | ─ | 4 | 0 | 1 | 9 | 7 | 5
Inadequate gas supply pressure | 1 | ─ | 1 | ─ | 1 | 1 | 3 | 1 | 1 | 3 | 3 | 4 | ─ | 1 | 5 | ─ | 2 | 1 | 6 | 11 | 20 | 60 | 69 | 19
Inadequate notice of replacement of metering installation and pilot relight service (Gas Distribution Code, Clause 6.2.1) | 3 | ─ | ─ | 4 | ─ | 1 | 1 | 0 | 0 | NOT CURRENT |  |  | ─ | ─ | ─ | ─ | ─ | 5 | 22 | 10 | 12 | NOT CURRENT
Property Damage (e.g. sprinkler systems, stormwater pipes) | 7 | 3 | 1 | 4 | ─ | 2 | 1 | 2 | 5 | 1 | 3 | 10 | 3 | 3 | ─ | 5 | 2 | 9 | 37 | 51 | 106 | 157 | 132 | 79
Reinstatement (inadequate or delayed) | 4 | 3 | 3 | ─ | ─ | 2 | 2 | 5 | 4 | 11 | 8 | 10 | 18 | 9 | 10 | 2 | 7 | 36 | 243 | 178 | 302 | 896 | 654 | 227
Re-lighting Appliances | ─ | 4 | ─ | 1 | 1 | 1 | 1 | 1 | 2 | NOT CURRENT |  |  | 1 | ─ | ─ | ─ | ─ | 2 | 7 | 16 | 28 | NOT CURRENT
Re-connection new tenant | ─ | 2 | ─ | ─ | 3 | ─ | 0 | 3 | 0 | NOT CURRENT |  |  | ─ | ─ | ─ | 1 | ─ | ─ | 2 | 17 | 6 | NOT CURRENT
Disconnection in error | ─ | ─ | ─ | ─ | ─ | 1 | 1 | 0 | 0 | NOT CURRENT |  |  | ─ | ─ | ─ | ─ | 2 | 3 | 2 | 10 | 9 | NOT CURRENT
Explanation for interruption to supply not provided within 20 business days of customer request (Gas Distribution Code, Clause 6.4.1) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | NOT CURRENT |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | NOT CURRENT
Timeliness of connection: previously connected (within 1 business day, Gas Distribution Code, Clause 3.1.1); | ─ | ─ | ─ | ─ | ─ | ─ | ─ | 2 | 0 | NOT CURRENT |  |  | ─ | 1 | ─ | ─ | ─ | ─ | ─ | 2 | 5 | NOT CURRENT
Timeliness of connection: new connection (as agreed with customer, or, where no date is agreed, within 20 business days, Gas Distribution Code, Clause 3.2.1) | 1 | ─ | ─ | ─ | ─ | ─ | ─ | 0 | 0 | NOT CURRENT |  |  | ─ | ─ | ─ | ─ | ─ | ─ | ─ | 0 | 0 | NOT CURRENT
Any other relevant matter | ─ | 2 | 1 | 5 | 12 | 7 | 17 | 21 | 22 | 35 | 51 | 69 | 3 | 6 | ─ | ─ | 16 | 13 | 96 | 257 | 622 | 889 | 938 | 719
Inlet/Meter Location | ─ | 1 | ─ | ─ | ─ | ─ | N/A |  |  | NOT CURRENT |  |  | ─ | ─ | ─ | ─ | ─ | ─ | N/A |  |  | NOT CURRENT
Requirement for Gasfitter's Licence Number to order connection | 1 | ─ | ─ | ─ | ─ | ─ | N/A |  |  | NOT CURRENT |  |  | ─ | ─ | ─ | ─ | ─ | ─ | N/A |  |  | NOT CURRENT
Complaints received via the Office of Technical Regulator | ─ | ─ | ─ | ─ | ─ | ─ | N/A |  |  | NOT CURRENT |  |  | ─ | ─ | 4 | ─ | ─ | ─ | N/A |  |  | NOT CURRENT
TOTAL | 19 | 15 | 6 | 16 | 18 | 15 | 26 | 35 | 34 | 50 | 65 | 95 | 26 | 21 | 19 | 9 | 30 | 69 | 419 | 552 | 1111 | 2011 | 1800 | 1049 | 0
Back to Index